Accredited Standards Committee
X3, Information Processing Systems

Doc: 	95a190r1
Date:	October 31, 1995
Project:	X3T10.1 / D
Ref Doc.:	SSA-PH1 rev 5a 
Reply to:	Paul PetersenPaul Petersen

To: 	   	X3T10.1 Membership
From:	Paul PetersenPaul Petersen {paul.petersen@conner.com}

Subject: Precharge Changes

8.7.1.1.5  Internal power bay connections

No pin shall exceed 2.25 A peak, 1.5 A continuous.

When a discharged device is hot plugged into a power distribution system, the capacitance in the decoupling capacitors on the printed circuit board causes significant current surges while the capactance is charging.  This current spike can cause arcing and damage the connector pads, as well as cause a voltage drop in the power distribution system that may affect other devices using the system for power.  To help this problem, pins 1, 2, and 16 have a resistor or other circuitry in series between the power source and the device connector (not on the device).  Additional current limiting circuitry may also be on the device.  This allows for a more controlled current draw as the device is being hot plugged.  These pins are longer to allow them to mate prior to the other voltage pins.  It is up to the implementator to determine the proper circuitry to add to these lines to meet the current draw limitations of the connector specified in this section.